## Tripping Log
Unnamed: 0 | Engine | Date | Time | Running hours | Details | Year | Month | Why 1 | Action Taken
| G2 | 2025-11-05 |  |  | Solenoid Valve | 2025 | 11
| Blackout | 2025-10-18 | 22:10:00 |  | Gas Generator Control Panel 2: due to malfuctioning of Voltage Level Relay(DC-27), master panel power supply OFF so replaced with new one. After that system behaviour is normal. | 2025 | 10
| G5 | 2025-10-18 |  |  | Relay issue | 2025 | 10
| G6 | 2025-10-18 |  |  | Relay issue | 2025 | 10
| G9 | 2025-10-12 | 17:00:00 |  | Engine tripped on circuit breaker operated. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced throttle with repaired one and back onload normal. | 2025 | 10
| G3 | 2025-10-08 | 12:00:00 | 116073 | Engine tripped on throttle acutator abnormal update rate (1440-9). Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6. Replaced throttle with repaired one and back onload normal. | 2025 | 10
| G8 | 2025-10-01 | 19:12:00 | 40744 | Engine tripped on detonation shutdown unit # 12 (E432-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced unit # 12 spark plug with new and taken onload. | 2025 | 10
| G8 | 2025-09-19 | 18:42:00 | 40454 | Engine tripped on detonation unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced drtonation sensor with new one/ spark plug replaced with old one then taken onload. | 2025 | 9
| G4 | 2025-09-15 | 11:20:00 | 96951 | Engine on Rear bearing temperature high. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Juction box connections found malfuctioning so re-tighted all connections then taken onload. | 2025 | 9
| G4 | 2025-09-15 | 18:00:00 | 96952 | Engine again tripped on same fault; Rear bearing temperature high. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Just bypass both side bearing temperature sensor then taken onload. | 2025 | 9
| G9 | 2025-09-13 | 07:40:00 | 9944 | Engine tripped Engine fuel differential pressure: Low: most serve (3) 1391-1/ Engine fuel differential pressure: Low: moderate severity (1) 1391-18. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. (removed gas regulation diaphram impact found normal. engine try to start but found gas street soliod only one valve operate. removed and checked solinoid connection and inspect harness found normal. cleaned ECM box's mounted harness connnection after that both solinoid valves operate normal. engine tested on 1650kw found all parameters with in range. | 2025 | 9
| G5 | 2025-09-12 | 06:45:00 | 100261 | Engine again tripped on High Left Terbocharger Turbine Outlet Temprature ( E243-3), High Left Terbocharger Turbine Outlet Temprature: Voltage Below Normal ( 1489-4), High Left Terbocharger Turbine Outlet Temprature: Current Below Normal ( 1489-5). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Terbocharger Turbine Outlet Temprature sensor harness found short so fixed with PVC tape and engine started and taken onload. | 2025 | 9
| G3 | 2025-09-05 | 18:30:00 | 115571 | Followup from dated 22.08.2025 tripping; Engine again tripped on fuel mertering module: current below normal (1446-5) and fuel mertering module: failure (1446-12). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. so again fuel valve replaced on dated 08.09.2025 with repaired one by Munfrid enginnering, after that engine behaviour found normal. | 2025 | 9
| Blackout | 2025-08-23 | 00:40:00 | B | Blackout due to short circuit in KE utility 1(Q2). as per Enercon report; G9 tripped on over current 1st then other engines tripped by Terberg on phase protections. | 2025 | 8
| Blackout | 2025-08-22 | 11:20:00 | B | Blackout due to Enercon Master Panel and gas engine control panel 02's Battery charger failure.( enercon system complete down). | 2025 | 8
| G3 | 2025-08-22 | 16:30:00 | 115248 | after balckout engine started and taken on load but load variation observed from 300 to 900Kw so stoped the engine and replaced manifold inlet pressure sensor and its harness with new one but problem still. as per allied replaced fuel valve with repaired one by Munfrid engineering, after half an hour engine tripped on fuel mertering module: current below normal (1446-5) and fuel mertering module: failure (1446-12). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. so again fuel valve replaced with repaired one by Munfrid enginnering, after that engine behaviour found normal. | 2025 | 8
| G8 | 2025-08-17 | 20:00:00 | 39716 | Engine tripped on detonation shutdown unit # 01. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. interchanged spark plug with unit # 04 and taken onload. After 01 hr detonation appear on unit # 04 so replaced spark plug with new one in respective unit and taken onload. | 2025 | 8
| G8 | 2025-08-10 | 21:52:00 | 39553 | Engine tripped on detonation shutdown unit # 12 (E432-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced unit # 12 spark plug with new and taken onload. | 2025 | 8
| G5 | 2025-08-08 | 05:10:00 | 99680 | Engine tripped on Emergency stop activated (E 264-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Reset engine and taken on load. | 2025 | 8
| G5 | 2025-08-08 | 09:28:00 | 99685 | 2nd time again Engine tripped on Emergency stop activated (E 264-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Laydown new emergency stop wire from connector to ECM and taken on load. | 2025 | 8
| G8 | 2025-08-01 | 19:10:00 | 39336 | Engine tripped on detonation shutdown on unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced detonation sensor with used one preventively and replaced spark plug with new. | 2025 | 8
| G5 | 2025-07-30 | 12:35:00 | 99501 | 3rd time Engine tripped on fuel metering module failure(1446-12), fuel metering module: current below normal(1446-5). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced main harness with new one due to suspected. | 2025 | 7
| G5 | 2025-07-28 | 08:15:00 | 99482 | Engine tripped on fuel metering module failure(1446-12), fuel metering module: current below normal(1446-5). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Thottle connector found loose so retighted and Reset engine then taken onload. | 2025 | 7
| G5 | 2025-07-15 | 08:25:00 | 99273 | Engine tripped on compressor bypass valve actuator: abnormal update rate(1720-9), fuel metering module failure(1446-12), throttle actuator: abnormal update rate(1440-9). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced overhauled fuel valve (from munfrid engineering) and replaced throttle harness with new one preventively. | 2025 | 7
| G1 | 2025-07-09 | 20:30:00 | 133820 | Engine tripped on unit # 18/20 detonation sensor failure. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced sensor with new one and back onload normal. | 2025 | 7
| Blackout | 2025-07-07 | 14:48:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 6, 7, 8, 9) running on normal load, Black shutdown occurred. Gas engine # 05' Red and neutral wire found broken, NDE side bearing bkoken and DE side bearing slipped. | 2025 | 7
| G3 | 2025-07-05 | 08:54:00 | 114161 | Engine tripped on lube oil diff. pressure low. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced both side sensors with ones and back onload normal. | 2025 | 7
| G1 | 2025-07-02 | 10:30:00 | 133647 | Engine tripped on throttle and acutator bypass abnormal update rate. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced throttle with repaired one and back onload normal. | 2025 | 7
| G1 | 2025-07-01 | 22:20:00 | 133635 | Engine tripped on unit # 06 detonation sensor failure. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced sensor with new one and back onload normal. | 2025 | 7
| Rental Eng. | 2025-06-21 | 03:28:00 | 53662 | Engine tripped on exhaust temprature high unit # 01. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. just disconnected thermocouple and taken onload. | 2025 | 6
| Blackout | 2025-06-21 | 20:48:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 6, 8, 9 and rental engine) running on normal load, Black shutdown occurred. No any reason found. | 2025 | 6
| G9 | 2025-06-16 | 13:00:00 | 7838 | Engine tripped on Jw inlet temprature high (during project team work). Load Shed Activated(Plant Lighting and Ventilation Load) with FP6 and CPP feeder. Just reset and taken onload. | 2025 | 6
| G3 | 2025-06-15 | 22:15:00 | 113684 | Engine tripped on throttle actuator failure. Load Shed Activated(Plant Lighting and Ventilation Load) with FP6 and CPP feeder. throttle found jamed so Replaced throttle with repaired one( repaired by munfrid engineering) then started and taken onload. | 2025 | 6
| G6 | 2025-06-14 | 23:30:00 | 99698 | Engine tripped on engine oil temprature high to coolant differance. Load Shed Activated(Plant Lighting and Ventilation Load) with FP6 and CPP feeder. Checked and found jacket water temprature sensor rusty so replaced with old one then started and taken onload. | 2025 | 6
| G4 | 2025-06-10 | 03:00:00 | 94855 | Engine tripped on CDVR shutdown. Load Shed Activated(Plant Lighting and Ventilation Load) with Ereema4 and complete CPP feeder. Total load cut @ 800kw due to only line 4 was running during eid holidays. Checked main alternator wires/ CTs controlling and rectifier plate. rectifier plate's one wire found broken so fixed then started and taken onload. | 2025 | 6
| G9 | 2025-05-31 | 10:45:00 | 7457 | Engine tripped during line5 sudden complete off (@ 5000Kw load reduced). Load Shed Activated(Plant Lighting and Ventilation Load) with Ereema4. | 2025 | 5
| G2 | 2025-05-30 | 09:10:00 | 117018 | Gas engine # 01 Tripped on Protection Relay(L1, Red). Load Shed Activated(Plant Lighting and Ventilation Load) with Ereema4. replaced with New protection relay with new brand(DEIF, S/N 2137441.0001/ Type: RMC-131D/ Order# 921005295.30/ Item 2913160660.01) provided by Enercon and installed by Mr. Rizwan (Enercon staff). new relay connections diagram attached in Terberg drawing. | 2025 | 5
| G1 | 2025-05-26 | 03:10:00 | 132841 | Engine 1 tripped on multiple cylinders low /high deviation and back fired ,there was 2500kw load jerkobserved from plant side (Line 5 emergency stopped) at that moment G1 tripped. Load Shed Activated.(Plant Lighting and Ventilatilation) with Ereema4. After that when they start the Genset deviating low alarms appeared in different cylinders.Check the engine parameters and sensors, after wiggle test found manifold pressure values changes. Check main harness and CAN resistance found normal. Start the Genset found throttle went to 100% and engine went to under speed. For testing purpose lay down manifold pressure sensor wire. Also install new manifold pressure (P/No. 276-6793) supplied by the customer. Also adjust fuel parameters from 995 BTU to 900 BTU. After doing so start the Genset found started normally check all parameters found normal then Genset put on load up to 1200kW found running normally check all parameters found normal. | 2025 | 5
| G1 | 2025-05-25 | 11:20:00 | 132828 | Engine tripped on turbo charger bypass valve actuator abnormal update rate. Load Shed Activated.(Plant Lighting and Ventilatilation) with Ereema4. Replaced Bypass actuator valve replace with G7 (G7 already on TE),reset the engine and back onload normal. | 2025 | 5
| G9 | 2025-05-23 | 14:05:00 | 7268 | Engine tripped on turbo1 temperature high (681 temperature), there was an 850 kW load on Gas Engine9. Load Shed Activated.(Plant Lighting and Ventilatilation) with Ereema4. Reset then Engine started/ kept as parallel to other engines. | 2025 | 5
| G1 | 2025-05-14 | 17:22:00 | 132572 | Engine tripped on Throttle abnormal update rate. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced preventively throttle harness with new one/ main harnesss slightly short near fuel valve connector so properly tapped then Engine started/ kept as parallel to other engines. | 2025 | 5
| G3 | 2025-05-11 | 22:20:00 | 113079 | Engine tripped on Engine oil diff. pressure low (E128-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. replaced oil assembly with engine # 07 (gas engine # 07 already on TE) then taken onload. | 2025 | 5
| Rental Eng. | 2025-04-22 | 11:55:00 | 53438 | Engine tripped on Deviation high unit # 08 and 10. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. adjusted BTU and correcting factor taken onload. | 2025 | 4
| G2 | 2025-04-21 | 11:40:00 | 116117 | Engine again tripped on CDVR shutdown( loss of excitation, reverse VAR). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Interchanged CDVR with gas engine # 07 for testing/ observation purpose (CDVR power supply interchanged from Terberg to Engine side) | 2025 | 4
| G9 | 2025-04-20 | 00:00:00 | 6481 | Engine tripped during gas engine # 07 junction box 25A breaker ON. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. just reset engine and engine 7 side 35A bearker off then engine 9 taken onload normally. | 2025 | 4
| Rental Eng. | 2025-04-17 | 10:35:00 | 53318 | Engine tripped on Detonation unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. adjusted BTU and correcting factor taken onload. | 2025 | 4
| G2 | 2025-03-24 | 17:45:00 | 115723 | Engine again tripped on CDVR shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. | 2025 | 3
| G2 | 2025-03-17 | 09:25:00 | 115554 | Engine tripped on CDVR shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked alternator main cables, CTs wires, any loosness; no any abnormality found. Check Exciter, PMG, Rectifier and sensing wires found normal./ At the time of visit on site gen set was in stop condition, customer complained that Genset was trip with Terberg panel alarm of Cdvr shutdown and Cdvr red LED was found blinking. Customer physical checked power cables terminals and rectifier plate found normal. Customer reset the Genset started and checked on load up to 500 kw found normal then off load and stop. AESL team check logged alarms in ET, no any recently shutdown was found in ET. Remove alternator cover and checked rectifier plate diodes and veristar found normal. Check and clean PMG and exciter wiring and installed back. Check PMG and exciter wiring in between wall mounted EMCP2 panel and alternator panel found a wire abrasion and Short to body ground marks the properly insulated the wire. Check and clean CDVR connectors and installed back. Installed back alternator cover and gen set started and check off load parameters found normal, genset put on load 500 kw and observed found normal, genset load increased Upto 850 kw found normal. | 2025 | 3
| G9 | 2025-03-16 | 16:16:00 | 131101 | Engine tripped on Earth Fault Trip Signal from Terberg 7. Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with CPP Thread Mode. Just Re-set engine then taken onload. | 2025 | 3
| Blackout | 2025-03-14 | 02:36:00 | B | all gas engines ( GE1, 2, 3, 4, 6,7, 8, 9 and rental engine) running on normal load, Black shutdown due to gas engine 7 yellow HT wire break and main coupling damage. | 2025 | 3
| Blackout | 2025-03-11 | 23:20:00 | B | all gas engines ( GE1, 2, 3, 4, 6,7, 8, 9 and rental engine) running on normal load, Black shutdown due to gas engine 7 red HT wire break. | 2025 | 3
| G1 | 2025-03-07 | 16:16:00 | 131101 | Engine tripped on detonation unit # 05 voltage above normal. Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with CPP Thread Mode. Replaced respective detonation sensor with new one and engine taken onload. | 2025 | 3
| Blackout | 2025-03-04 | 08:15:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 6,7, 8 and 09) running on normal load, Black shutdown due to gas engine 5 blue HT wire break. | 2025 | 3
| Rental Eng. | 2025-03-04 | 16:15:00 | 52951 | Engine tripped on over speed. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. One CT found damage so replaced with new one and taken onload. | 2025 | 3
| G6 | 2025-03-03 | 07:30:00 | 97255 | Engine tripped on detonation unit # 15. Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with CPP Thread Mode. Replaced respective detonation sensor due to wire damage and engine taken onload. | 2025 | 3
| G8 | 2025-02-23 | 00:45:00 | 36596 | Engine tripped on over speed. Load Shed Activated.(Plant Lighting and Ventilatilation), FP6 with CPP. No any abnormality found so just re-set engine then taken onload. | 2025 | 2
| G2 | 2025-02-23 | 05:10:00 | 115093 | Sunden load veriation observed from 1300 to 400kw. Load Shed Activated.(Plant Lighting and Ventilatilation) FP6 with CPP Thread Mode. Customer complained about load variation problem. Check the historical alarms and graphs. For testing Interchange throttle actuator and fuel valve from other Genset. Also install new compressor bypass actuator motor and couple the old shaft. Remove tappet covers ignition transformers and spark plugs. Install new spark plugs (P/No. 602-7619, Qty = 20) in all cylinders. After doing so install back all ignition transformers and tappet covers. Lay down new wires for voltage and speed control. Also ENERCON engineer visit the site and interchange DEIF Generator controller from other Genset panel. After that start the Genset found started normally check all parameters found normal then Genset put on load up to 800kW found after some time Terberg engine parameters disappeared as well as the data of EMCP II+ disappeared. Offload stopped the Genset. Change datalink wire but no data appeared. Change CCM (new) and EMCP from other Genset but problem remain same. However when Terberg data link removed EMCP parameters appeared. Start the Genset and put on load up to 1000kW found running normally. EMCP to Terberg communication problem need to be addressed | 2025 | 2
| G3 | 2025-02-16 | 03:10:00 | 111214 | Engine again tripped on fuel metering module failure. Load Shed Activated.(Plant Lighting and Ventilatilation) and CPP Thread Mode with FP6. Just reset engine and taken onload under observation on 600kw after satisfactory operation engine kept as parallel to other engines. | 2025 | 2
| G3 | 2025-02-16 | 16:10:00 | 111222 | Engine 3rd time again tripped on fuel metering module failure. Load Shed Activated.(Plant Lighting and Ventilatilation) and CPP Thread Mode with FP6. Replaced fuel valve with an other repaired one (Repaired from Munfrid Engineering). after work engine started and taken onload under observation on 600kw after satisfactory operation engine kept as parallel to other engines. Preventively Throttle Harness (p# 305-0580) replaced with new one due to threads damage. | 2025 | 2
| G3 | 2025-02-15 | 02:05:00 | 111200 | Engine tripped on fuel metering module failure. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. Replaced fuel valve with repaired one (Repaired from Munfrid Engineering). after work engine started and taken onload under observation on 600kw after satisfactory operation engine kept as parallel to other engines. | 2025 | 2
| G2 | 2025-02-07 | 00:20:00 | 115083 | Sunden load veriation observed from 1100 to 100kw. After inspection unit # 01, 02, 05, 07, 09, 11, 15, 17, 18 compression found zero. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. | 2025 | 2
| G4 | 2025-02-07 | 21:30:00 | 92384 | Engine tripped on deviation low unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. Just cleaned spark plug and check transformer resisitance, found ok. Preventively disconnected respective thermocouple engine taken onload. | 2025 | 2
| G4 | 2025-01-28 | 15:15:00 | 35599 | Engine tripped on detonation unit # 12 and 9 hours ago Transformer primary 8 Current above normal apprear. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced unit # 8 transformer with old one and unit # 12 spark plug cleaned then engine started normally | 2025 | 1
| N1 | 2025-01-27 | 15:40:00 | 42931 | Follow from 26.01.2025 Niigata 1 Tripping; GaddiBaan satff replaced Governor but same load veriation as per previous and Engine tripped on load veriation 200 to 900kw. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked fuel pressure, temperature found ok. Cleaned indication filter, flow meter filter and main filters but problem as it is. | 2025 | 1
| N1 | 2025-01-26 | 15:40:00 | 42931 | Engine tripped on load veriation 200 to 900kw. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked fuel pressure, temperature found ok. Cleaned indication filter, flow meter filter and main filters but problem as it is. | 2025 | 1
| Rental Eng. | 2025-01-15 | 17:10:00 | 52553 | Engine tripped on detonation unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced sensor with new one and taken onload. | 2025 | 1
| G2 | 2025-01-05 | 16:35:00 | 114336 | Engine tripped on GECM shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. On ET detonation Derate requested (E253-2) and detonation appear on unit # 11, 07, 17, 09, 05, 10 and 18. engine tripped on unit # 11 but secondry voltage was down in unit # 05( from 25 to 19.7)/ Check alarm history, detonation alarm found in several cylinders and and genset tripped on cylinder no. 11 detonation shutdown.Remove all cylinders ignition transformers, spark plugs.Inspect the cylinders no. 05 & 07 with bore scope found satisfactory.Measure the all cylinders compression pressure found between 240psi to 260psi. Check and adjust the valves clearance of cylinder no. 05 & 07. Swap the cylinder no. 05/07 detonation sensor with cylinder no. 02/04. Swap the ignition transformers of cylinder no. 05/07 with 08/14. Swap the spark plugs if cylinder no. 05/07 with 18/10. Start the genset and put on load upto 1300kw, maximum providing load by customer due to unavailability of load shed. check all running parameters found satisfactory. (43 times detonation alarm appears at cylinder no. 05 between 111268 to 114340 hours) | 2025 | 1
| G5 | 2025-01-02 | 17:15:00 | 96984 | Engine tripped on GECM alarm. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. No alarm on ET and Terberg, Reset engine taken onload normally | 2025 | 1
| G8 | 2024-12-19 | 08:15:00 | 35726 | Engine tripped due to gas pressure low (97mbar on gas engine #03). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Reset engine taken onload normally | 2024 | 12
| G2 | 2024-12-18 | 09:25:00 | 113908 | Engine tripped on CDVR shutdown (2 hours before warning appear as current high (slow). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked alternator main cables, CTs wires, any loosness; no any abnormality found. Check Exciter, PMG, Rectifier and sensing wires found normal. Replaced CDVR with new one with configured then engine started normally. ( Old CDVR part # 235-5725, New CDVR part # 314-7755). | 2024 | 12
| G8 | 2024-12-13 | 15:15:00 | 35599 | Engine tripped on detonation unit # 01 (voltage above normal: 1501-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced respective sensor with new one then engine started normally | 2024 | 12
| Rental Eng. | 2024-12-11 | 19:35:00 | 52135 | Engine tripped on throttle abnormal behavior . Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Re-tight throttle and taken onload. | 2024 | 12
| Rental Eng. | 2024-12-09 | 03:10:00 | 52100 | Engine tripped on throttle abnormal behavior . Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6.. Re-tight throttle and taken onload. | 2024 | 12
| Blackout | 2024-12-06 | 03:36:00 | B | gas engines running on normal load, Black shutdown due to 3520 h tripped. | 2024 | 12
| G7 | 2024-12-02 | 19:20:00 | 84296 | Engine tripped. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. after investigation, tghrottle found loose so re-tight then taken on load. | 2024 | 12
| G8 | 2024-11-26 | 13:15:00 | 35419 | Engine tripped on detonation unit # 01. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. after investigation unit # 01 cylinder head found damage so replaced with repaired one. and replaced liner/ piston complete set with new one on dated 27.11.2027. After that engine started normally | 2024 | 11
| G3 | 2024-11-26 | 19:35:00 | 109364 | Engine tripped on jacket water temprarture high. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. after investigation, its j/w pump found damage so replaced with repaired one then taken on load. | 2024 | 11
| Rental Eng. | 2024-11-24 | 20:40:00 | 51990 | Engine tripped on throttle abnormal behaviour . Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6.. Repalced throttle actuator. 2. Replaced compressor bypass valve. 3. Replaced All spark plugs. 4. 2 nos thermocouple replaced of cyl 01&03 5. Air elements cleaned. 6. valve lash carried out. 7. Adjust Gas parameters on load. 8. Flash cooling system and fill fresh NGEC. replaced throttle with old one then taken onload. | 2024 | 11
| Rental Eng. | 2024-11-20 | 11:00:00 | 51888 | Engine tripped on cylinder # 10 detonation sensor; voltage above normal(1510-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. replaced respective detonation sensor with new one then taken onload. | 2024 | 11
| Rental Eng. | 2024-11-17 | 23:55:00 | 51845 | Engine tripped on detonation shutdown unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. replaced respective detonation sensor then taken onload. | 2024 | 11
| Rental Eng. | 2024-11-12 | 13:10:00 | 51718 | Engine tripped on deviation low shutdown unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. replaced respective transformer and spark plugs then taken onload. | 2024 | 11
| Rental Eng. | 2024-11-10 | 01:40:00 | 51684 | Engine tripped on detonation shutdown unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. Just reset engine and taken onload. | 2024 | 11
| Blackout | 2024-11-09 | 11:25:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 7 and 09) running on normal load, Black shutdown due to 3520 h tripped. | 2024 | 11
| G9 | 2024-11-09 | 17:55:00 | 2518 | Engine tripped/ load dropped from 1700 to -320kw. All load shed activate and additional CPP whole breaker cut by manually and save an other blackout. (its fuel solinoid valve power supply found malfuctioning so checked and re-tight After that engine started normally). | 2024 | 11
| G5 | 2024-11-02 | 02:30:00 | 95532 | Engine tripped on detonation unit # 09. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP. checked transformer and spark plug found ok, then just re-set engine and taken onload. | 2024 | 11
| G5 | 2024-11-02 | 22:00:00 | 95543 | Engine tripped on detonation unit # 11. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP and FP6. checked transformer and spark plug found ok, checked respective exhaust clamps found ok. Replaced detonation sensor with new one due to all three wires found melted. | 2024 | 11
| Rental Eng. | 2024-10-25 | 22:10:00 | 51636 | Engine tripped on detonation shutdown unit # 09. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6 and CPP. Just reset engine and taken onload. | 2024 | 10
| G8 | 2024-10-24 | 16:00:00 | 34928 | Engine tripped on over speed. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP. No any abnormality found so just re-set engine then taken onload. | 2024 | 10
| G6 | 2024-10-22 | 20:26:00 | 96808 | Engine tripped on detonation unit # 07. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP and FP6. checked transformer and spark plug found ok, Replaced detonation sensor with new one due to one wire melted. | 2024 | 10
| G2 | 2024-10-19 | 05:26:00 | 112533 | Engine tripped on lube oil pressure low. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP. Damper side oil leakage observed. | 2024 | 10
| G2 | 2024-10-14 | 13:40:00 | 112424 | Engine tripped on CDVR shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6 and CPP. No any alarm on ET and EMCP-II. Checked alternator main cables, CTs wires, any loosness; no any abnormality found so reset engine and taken onload @500kw on instruction of Tehseen sb./ Customer complained about engine tripping at CDVR SHUTDOWN. Check all engine and CDVR parameters found normal. Asked the customer to offload and stopped the Genset, customer did the same. Check CDVR program found normal. Check CDVR harness found normal. Check Exciter, PMG, Rectifier and sensing wires found normal. For testing interchange Alarm and shutdown wires from both EMCP and terberg sides as well as interchange their respective relays in Terberg panel. Check kW transducer found working normally. After doing so start the Genset found started normally check all parameters found normal then Genset put on load up to 1250kW found running normally check all parameters found normal. | 2024 | 10
| G1 | 2024-10-06 | 03:35:00 | 127761 | Engine tripped on unit # 01deviation low. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6 and CPP Thread Mode. unit # 01 transformer interchanged with unit # 15 and spark plug with unit # 11. checked thermocouple harness found ok. Checked unit # 01 cylinder head pressure found normal after completion of work start the genset check all parameters found normal genset put on load up to 1100 available load. | 2024 | 10
| Rental Eng. | 2024-10-06 | 13:40:00 | 51506 | Engine tripped on detonation shutdown unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6 and CPP. Just reset engine and taken onload. | 2024 | 10
| G1 | 2024-10-06 | 17:00:00 | 127765 | Followup from same date on 3:35:00 AM: allied team inspected and engine taken onload @ 500kw for 3 hours no any abnormality found but engine again tripped on same alarm within one hour on 1100kw. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6 and CPP. Replaced thermocouple harness(220_2340) with new one and ITSM with repaire one. After completed work start engine and put on load up to "1450" kw . All system parameters working under limit. | 2024 | 10
| G2 | 2024-09-12 | 06:02:00 | 111675 | Engine tripped on unit # 5 detonation. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. Customer complaint about Detonation appear different cylinder. And Cylinder # 5 detonation shutdown. & cylinder number 18 exhaust temperature high. Connect the ET and Check codes. Remove the all units Valve cover with ignition transformers. All spark plugs. Perform Boroscope of all units. Found no any abnormality observe Check and adjust valve bridge and valve lash. Check cylinder number 18 exhaust thermocouple and harness found ok. But Cylinder #5 install new thermocouple. And install old thermocouple cylinder number 16 because exhaust temperature variation. Install back all spark plugs with new gaskets. Install back Valve cover with ignition transformer. After completion of work start the genset. Genset started normal then put on load UpTo 1700kw check all running parameters found normal cylinder number 16 exhaust temperature normal & Cylinder #5 check detonation found normal no detonation.& All units exhaust temperatures normal no variation. Genset running satisfactory condition. | 2024 | 9
| G6 | 2024-08-30 | 11:45:00 | 95679 | Engine tripped on unit # 9/11 detonation. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. after inspection unit # 11 cylinder head found damage so replaced with repaired one then engine taken onload. At the time visit at Tri pack eng#6 found running normal on load but suddenly engine stop on detonation in unit #11 found spark plug damage remove the ignition transformer,bridge & rocker arm attachment and cylinder head found exhaust valve drop and damage to the piston upper area after removal piston & liner clean block internal and upper surface. Clean the new liner P/N 350-0074 and install with new kit as per cat procedure.Assemble the new piston P/N 376-7655 with new rings P/N 348-8779,223-6361, 347-1085 as per procedure.Install the piston in unit no 11 with new bearing P/N 107-7730 as per cat specification and procedure. Install the cooling jet and crank window.install the cylinder head with new gasket and torque as per cat specification and procedure.Install back related attachment and valve lash & bridge adjust as per cat procedure.Check the all cylinder head pressure found normal.after completion of work start the genset check all parameters found normal genset put on load up to 1100 available load. | 2024 | 8
| Blackout | 2024-08-26 | 00:50:00 | B | all gas engines running on normal load, Black shutdown due to 3520 h tripped (its fuel solinoid valve power supply found malfuctioning so checked and re-tight After that engine started normally). After shutdown gas engine 1 behaviour found abnormal, allied team taken comperassion for all cylinders; 11 units comperassion found zero so engine taken on TE overhauling. | 2024 | 8
| G8 | 2024-08-20 | 12:15:00 | 34255 | Engine tripped due to its cooling water pump tripped. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. after inspection respective breaker all three phase connection found loose. re-tight connections then engine taken onload. | 2024 | 8
| G8 | 2024-08-19 | 12:15:00 | 34241 | Engine tripped due to its transformer breaker tripped on transformer termprature high. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. in same time both engine (Gas engine 8 and 9) MCC main panel also tripped. removed transformer tripping wire then engine taken onload. (safe blackout) | 2024 | 8
| G6 | 2024-08-14 | 21:15:00 | 95379 | Engine tripped on deviation low unit # 10. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. checked and found unit # 10 head and liner/ piston found damage. Clean all new parts, install connecting rod in new piston p/N 376-7655, Install new piston Ring P/N 223-6361, 348-8779, 347-1085, Install piston Cylinder # 10. Install Liner sleeve P/N 591-7899, Install spacer plate & install new head gaskets, install rebuild cylinder head. & All attachments. Adjust valve bridge and valve lash. Install Spark plug.& Valve cover. Filled water of jacket water circuit & water heater on. All installation & torque perform as per cat procedure. And all new parts supplied by customer. After maintain temperature start the genset. Genset started normal check off load parameters found normal than genset put on load 1000 kw. All on load running parameters found normal genset running satisfactory condition. | 2024 | 8
| G9 | 2024-08-13 | 12:30:00 | 843 | Engine tripped due oil level low switch activated. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. just re-set (removed this alarm from Enercon panel for engine tripping now)engine then taken onload. | 2024 | 8
| G8 | 2024-08-08 | 16:30:00 | 34031 | Engine tripped due to Fingering by some champion(by Project Team) without my knowledge on 3516 C breaker . Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. just re-set engine then taken onload. | 2024 | 8
| G1 | 2024-08-05 | 22:15:00 | 127174 | Engine tripped on detonation during peak load( +1400kw). (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. engine re-set then started on load. | 2024 | 8
| G3 | 2024-07-28 | 10:40:00 | 106635 | Engine tripped on frequency low/ gas pressure low . Load Shed Activated.(Plant Lighting and Ventilatilation). just re-set engine then taken onload. | 2024 | 7
| G8 | 2024-07-24 | 08:00:00 | 33677 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. At the time of visit Genset was running on 1000kW load. Walk around inspection carried out. Customer complained about engine tripping this morning at Reverse power.Connect E.T check codes found none. Ask the customer to stopped the Genset. Customer stopped the Genset at 12 pm. Remove ECM Box, remove ECM and install other used ECM provided by the customer. Lay down new data link wire between ECM and EMCP-II+. Lay down auto, start, stop wires between ECM and EMCP-II+. Lay down GECM shutdown wire between ECM and Terberg. Externally ground the ECM. Check ECM harness power supply +ve & -ve along with keyswitch. After doing so flash the ECM, configure it and then start the Genset found started normally check all parameters found normal, then Genset put on load up to 1000kW found running normally check all parameters found normal. | 2024 | 7
| G8 | 2024-07-23 | 06:45:00 | 33658 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-23 | 10:00:00 | 33660 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| Rental Eng. | 2024-07-23 | 12:10:00 | 50676 | Engine tripped on frequency low. Load Shed Activated.(Plant Lighting and Ventilatilation). just re-set engine then taken onload. | 2024 | 7
| G8 | 2024-07-23 | 19:30:00 | 33663 | Engine again tripped on GG8 breaker operated/ GECM shutdown. (Load Shed Activated.(Plant Lighting and Ventilatilation). At the time of visit Genset was at stopped condition. Walk around inspection carried out. Held meeting with the customer. Discussed all the previous tripping and their remedial actions, it has been decided to use shunt coil as per recommendation of ABB representative. Logic has been implemented and then stoppage and engine safety check at breaker tripping. Replace the ITSM with customer provided repaired ITSM, due to found active alarm abnormal update rate After doing so start the Genset found started normally check all parameters found normal then Genset put on load up 1000kW found after half an hour it tripped. Check alarms found GECM shutdown, check data logger found no visible fault. However just for testing remove GECM shutdown wire and interchange their relays inside Terberg panel, after that genset has been started and put on load up to 1000kW found running normally check all parameters found normal, observe Genset for 3 hours found running normally. | 2024 | 7
| G8 | 2024-07-22 | 06:00:00 | 33637 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-22 | 10:20:00 | 33642 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-22 | 14:00:00 | 33643 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-22 | 19:45:00 | 33647 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-21 | 08:30:00 | 33623 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-20 | 13:40:00 | 33604 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-20 | 20:30:00 | 33611 | Engine again tripped on GG8 breaker operated. (Load Shed Activated.(Plant Lighting and Ventilatilation). engine re-set then started on load. | 2024 | 7
| G8 | 2024-07-19 | 00:20:00 | 33574 | Engine again tripped on voltage protection alarm within 3 hours. (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. engine re-set then started on 500kw. Next allied will come for further inspections. | 2024 | 7
| G5 | 2024-07-19 | 05:40:00 | 93111 | engine tripped on PO generator differential current. (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. just reset engine then taken on load but engine again tripped on same alarm. (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. after inspection of power cables/ control wires/ PMG/ diodes/ CDVR. every thing found nomal so engine started and taken onload @800kw. after 1 hour engine again tripped on same fault ( one phase difference found high@ 17). (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. after inspection of generation CTs, blue phase CT control wire found broken. cleaned and retighted wire. | 2024 | 7
| Semi blackout | 2024-07-18 | 12:12:00 | SB | Line 5: Gas engine 09 run Speretlty for load test after commisioning for line 5 only. ROCOF relay operated and KE breaker tripped and same time engine 9 tripped and blackout occurred in BOPP line 5 side. | 2024 | 7
| Blackout | 2024-07-18 | 17:00:00 | B | Followup from from same date KE load shift: gas engine 9 load dropped from 2200kw to 600kw due to gas pressure low. In same time all other engines tripped on frefuency low. | 2024 | 7
| G8 | 2024-07-18 | 21:40:00 | 33572 | Engine tripped on voltage protection alarm. (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. engine re-set then started. | 2024 | 7
| Semi blackout | 2024-07-17 | 18:53:00 | SB | sudden LG chiller tripped and Line 5 gone on scrap(Gas engine 09 run with KE Speretlty for load test for line 5 only). KE on reverse -460kw and gas engine load also decreased but engine tripped on turbo exhaust temperature and blackout occurred in BOPP line 5 side. | 2024 | 7
| G8 | 2024-07-16 | 10:24:00 | 33567 | Engine tripped on voltage protection alarm( engine was running on KE and gas engine 9). After reset engine started but shutoff valve found malfuctioning. Due to Muharram holidays Allied team come on dated 18.07.2024 and overhauled shutoff valve then engine started normally. | 2024 | 7
| Semi blackout | 2024-07-16 | 20:12:00 | SB | Line 5: Gas engine 09 run Speretlty for load test after commisioning for line 5 only. ROCOF relay operated and KE breaker tripped and same time engine 9 tripped and blackout occurred in BOPP line 5 side. | 2024 | 7
| Semi blackout | 2024-07-09 | 17:00:00 | SB | Line 5: Gas engine 08, Gas engine 09 run Speretlty for load test after commisioning for line 5 only. Gas engine 09 tripped on frequency low and other engine also tripped on overload and blackout occurred in BOPP line 5 side. | 2024 | 7
| G8 | 2024-07-07 | 19:15:00 | 33483 | tripped on voltage protection activated. Reset and started. | 2024 | 7
| G8 | 2024-07-06 | 10:00:00 | 33468 | engine tripped due to main MCC panel tripped. (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. | 2024 | 7
| G8 | 2024-07-06 | 12:00:00 | 33470 | engine again tripped due to main MCC panel tripped. (Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. | 2024 | 7
| Blackout | 2024-07-06 | 19:15:00 | B | due to again main MCC panel for gas engine 8 and 9 tripped from line 5 LT side. Both engine tripped.( project team replaced main MCC breaker with other one due to suspected. | 2024 | 7
| Blackout | 2024-07-05 | 08:35:00 | B | due to STP1 tripped and not reset. Removed gas engine 8 and 9 MCC panel supply from STP1 and connected with line5 LT room. | 2024 | 7
| G4 | 2024-07-02 | 15:40:00 | 87281 | Engine tripped on ignition transformer primary# 09: current below normal. Load Shed Activated.(Plant Lighting and Ventilatilation). Replaced respective transformer with old one then taken onload. | 2024 | 7
| N2 | 2024-06-28 | 16:45:00 | 107622 | engine tripped on low voltage (6000v). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. after inspection AVR found faulty. So replaced with niigata engine 1 and configure by Mr. waheed(electrical) and Mr. Ahtesham(Enercon). after that engine taken onload. | 2024 | 6
| Blackout | 2024-06-28 | 20:35:00 | B | due to Enercon panel GCM1 and GCM3 malfunctioning; gas engine 1 and 3 (gas engine 2 already stopped)tripped in same time this causes the blackout. After inspection panel 220v supply breaker found tripped. | 2024 | 6
| N2 | 2024-06-27 | 00:15:00 | 107606 | engine running onload @ 1200kw sudden load increased upto 1850kw. All parameters found normal. After some time manually load decreased by fuel handle then stopped engine manually, Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. After inspection engine link rod found damage so replaced with old spare one.then taken onload. | 2024 | 6
| Rental Eng. | 2024-06-11 | 22:30:00 | 49854 | Engine again tripped on detonation shutdown unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation). just re-set engine then taken onload but again tripped so tomorrow allied team will come for toubleshooting . | 2024 | 6
| Rental Eng. | 2024-06-10 | 00:35:00 | 49805 | Engine again tripped on detonation shutdown unit # 09. Load Shed Activated.(Plant Lighting and Ventilatilation). just re-set engine then taken onload. | 2024 | 6
| Rental Eng. | 2024-06-09 | 00:35:00 | 49805 | Engine again tripped on deviation low shutdown unit # 11. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. disconnected respective thermocouple then taken onload. | 2024 | 6
| G5 | 2024-06-09 | 17:22:00 | 92243 | Engine tripped on alternator bearing temperature high. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. checked by temprature gun found ok so de-active alarm then engine taken onload. | 2024 | 6
| Rental Eng. | 2024-06-08 | 22:50:00 | 49803 | Engine tripped on deviation low shutdown unit # 11. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. reset engine then taken onload. | 2024 | 6
| Rental Eng. | 2024-06-03 | 23:09:00 | 49693 | Engine tripped on detonation shutdown unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. reset engine then taken onload. | 2024 | 6
| Rental Eng. | 2024-05-24 | 17:45:00 | 49489 | Engine tripped on detonation shutdown unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. reset engine then taken onload. | 2024 | 5
| G2 | 2024-05-23 | 07:35:00 | 110739 | Engine tripped on diff cylinders very very hihg(up to 700+) and load veriation from 1950 to 1500kw. abnormal sound occured and engine tripped. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Check alarm history, found high jacket water temperature & high oil temperature alarms before seven hours, at yesterday shutdown Cylinder no. 01 spacer plate found damaged, removed spark plug, found water in cylinder Removed all cylinders valve covers, along with ignition transformers and spark plugs Manual purged the all cylinders found dry.Performed the Bore scoping test of all cylinders. Drain the jacket and auxiliary water. Removed the auxiliary water pump and attachments. Removed the unit no. 01 cylinder head, piston connecting rod and cylinder liner as per cat procedure. Removed all cylinder heads/ liners/ pistons and connecting rods for inspections. | 2024 | 5
| Blackout | 2024-05-22 | 17:15:00 | B | STP #01 tripped on over current relay, same time gas engine #0 tripped. After some time due to cooling towers and pums off, gas engine 2 and 3 also tripped and blackout. | 2024 | 5
| G5 | 2024-05-17 | 15:25:00 | 91694 | Engine tripped on deviation low unit # 19(E859-3) and ignition transformer primary # 19: current below normal(1754-5) . Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. replaced ignition transformer with old one then engine taken onload. | 2024 | 5
| G6 | 2024-05-15 | 13:30:00 | 93202 | Engine tripped on detonation shutdown unit # 09 during load testing after preventive maintenance. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. replaced detonation sensor with old one/ transformer and spark plug interchanged/reset engine then taken onload. | 2024 | 5
| Rental Eng. | 2024-05-14 | 09:50:00 | 49376 | Engine tripped on detonation shutdown unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation). Just reset engine and taken onload. | 2024 | 5
| G1 | 2024-05-06 | 17:45:00 | 125046 | Engine tripped on detonation shutdown unit # 18. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. just reset engine then taken onload. | 2024 | 5
| G1 | 2024-05-04 | 22:50:00 | 125004 | Engine tripped on detonation shutdown unit # 18. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. repleced unit # 18 transformer then taken onload. | 2024 | 5
| Blackout | 2024-05-02 | 14:10:00 | B | gas engine # 01, 03, 04, 05, 06 and 07 running onload 1300~1350 kw. Due to sloar dip from 2600 to 1000kw in few seconds one one all engine tripped. | 2024 | 5
| G4 | 2024-04-30 | 11:00:00 | 85782 | Engine tripped on detonation shutdown unit # 10(1510-4: voltage below normal). Load Shed Activated.(Plant Lighting and Ventilatilation). replaced sensor with used one | 2024 | 4
| G5 | 2024-04-30 | 14:40:00 | 91292 | Engine tripped on ignition transformer primary #05: current above normal(305-6). Load Shed Activated.(Plant Lighting and Ventilatilation). replaced ignition transformer with used one. | 2024 | 4
| Rental Eng. | 2024-04-26 | 10:43:00 | 49057 | Engine tripped on detonation shutdown unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Just reset engine and taken onload. | 2024 | 4
| G5 | 2024-04-23 | 20:10:00 | 91142 | Engine tripped on compressor bypass/ throttle abnormal updates. Load Shed Activated.(Plant Lighting and Ventilatilation). Just reset engine then taken onload | 2024 | 4
| G3 | 2024-04-16 | 13:45:00 | 104188 | Engine tripped on deviation low unit # 08. Load Shed Activated.(Plant Lighting and Ventilatilation). Replaced unit # 8 transformer with used one. | 2024 | 4
| G3 | 2024-04-15 | 11:05:00 | 104175 | Engine tripped on overspeed. Load Shed Activated.(Plant Lighting and Ventilatilation). main couplung found damaged so replaced with engine # 02 coupling(which already on accident, engine 2 coupling R.Hrs. 7789 ) | 2024 | 4
| G4 | 2024-03-28 | 00:08:00 | 84981 | Engine tripped on detonation shutdown unit # 10. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. checked transformer/ spark plug found normal. Preventively replaced detonation sensor with new one and taken onload. | 2024 | 3
| G4 | 2024-03-28 | 00:08:00 | 84981 | Engine tripped on detonation shutdown unit # 10(voltage above normal). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Just reset engine taken onload. | 2024 | 3
| Rental Eng. | 2024-03-27 | 17:55:00 | 48769 | Engine tripped on detonation shutdown unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Just reset engine and taken onload. | 2024 | 3
| G3 | 2024-03-25 | 21:10:00 | 124121 | Engine tripped on detonation shutdown unit # 18. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Just reset engine and taken onload normally. | 2024 | 3
| G3 | 2024-03-19 | 18:55:00 | 103546 | Engine tripped on generator output power sensor: voltage above normal(1719-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Checked and found EMCP-II malfuctioning so replaced engine # 02(which already on accident) panel/ Check EMCP supply and EMCP switching supply found 24Vdc. Try to reset the EMCP but display remain blank hence EMCP found faulty.Brief the customer to arrange EMCP customer advised to interchange EMCP from other Genset. Remove wiring of EMCP along with EMCP module. Install EMCP from other Genset. Switch on the supply found EMCP working normally. Customer also complained about CYL.# 6 detonation sensor code, in this regard they already installed new detonation sensor but problem again repeat. Lay down detonation sensor wire from Cyl.# 6 to ECM. After doing so start the Genset found started normally check all parameters found normal then Genset put on load up to 1150kW found running normally check all parameters found normal. | 2024 | 3
| G3 | 2024-03-15 | 06:15:00 | 103462 | Engine tripped on Detonation Unit # 06 (1506, voltage above normal 1506-3/ voltage below normal 1506-4). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Replaced Sensor with new one, engine taken on load. | 2024 | 3
| G6 | 2024-03-08 | 15:40:00 | 91626 | Engine tripped on DE bearing temperature high. Load Shed Activated.(Plant Lighting and Ventilatilation). Reset engine and deactive respective sensor and greased both side then engine taken on load. | 2024 | 3
| G5 | 2024-03-08 | 18:40:00 | 90070 | Engine tripped on compressore bypass abnormal updates. Load Shed Activated.(Plant Lighting and Ventilatilation). Reset engine/ checked harness/ retighted connectors then engine taken on load. | 2024 | 3
| G4 | 2024-03-02 | 12:15:00 | 84408 | Engine tripped on Deviation low unit # 10. Load Shed Activated.(Plant Lighting and Ventilatilation). Reset engine and removed thermocouple then engine taken on load. | 2024 | 3
| G1 | 2024-02-28 | 01:50:00 | 123641 | Engine tripped on Detonation Unit # 18. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Replaced detonation sensor with new one and transformer with old one then engine taken on load. | 2024 | 2
| G1 | 2024-02-25 | 15:25:00 | 123565 | Engine tripped on Devation low Unit # 19. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Disconnected thermocouple then engine taken on load. | 2024 | 2
| G5 | 2024-02-25 | 09:15:00 | 89832 | Engine tripped on Detonation Unit # 17 with different unit warning appear. Load Shed Activated.(Plant Lighting and Ventilatilation). after reset engine started taken onload 500kw but again tripped on same alarms. Replaced all spark plugs with new one then engine started but same behaviour. readjusted fuel parameters as per Tehsin sb instaruction but same behaviour and unit # 14 exhaust temperature very high(more then 700) so taken compression for all units found unit # 14 low and unit # 05 zero, so replaced cylinder heads with sapre ones (from gas engine # 02. gas engine #02 already on accident. See 19.02.2024 engine 2 tripping) | 2024 | 2
| N2 | 2024-02-25 | 22:00:00 | 106822 | Engine tripped on Middle fault(under frequancy). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Due to fuel pressure very low on HFO(Checked and found indication filter and near flow meter filter choked.) engine tripped. In same time gas engine 3 also tripped on under frequancy.( line 4 and CPP 1 also tripped on low frequancy). | 2024 | 2
| G3 | 2024-02-25 | 22:00:00 | 106822 | Engine tripped on Middle fault(under frequancy). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Due to fuel pressure very low on HFO(Checked and found indication filter and near flow meter filter choked.) engine tripped. In same time gas engine 3 also tripped on under frequancy.( line 4 and CPP 1 also tripped on low frequancy) | 2024 | 2
| G3 | 2024-02-20 | 05:58:00 | 102905 | Engine tripped on Detonation Unit # 06 (1506, voltage above normal 1506-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Replaced Sensor with new one, engine taken on load. | 2024 | 2
| G2 | 2024-02-19 | 05:58:00 | 110562 | Gas engine #02 load dropped suddenly and heavy sound from engine. Stop the emergency engine on load. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Customer complained about abnormal sound from the engine hence they stopped the Genset. Check the engine found crank case window damaged of unit number 3,4,5. Check connecting rod found damaged of unit no. 4. Cooling jets also found damaged of unit number 3 and 4. Cylinder number 4 head has been removed found intake valve damaged, piston crown damaged, rocker arm assembly damaged. Oil found mixed with water also crankshaft counter weight found damaged. Meet with customer and describe whole situation and briefed that engine will be dismantled whit out main Alternator. And sent to AESL for further inspection. Check and save all the data, graphs and taken out PSRT. | 2024 | 2
| G2 | 2024-02-18 | 08:30:00 | 110542 | Engine tripped on Gen protection relay. Load Shed Activated.(Plant Lighting and Ventilatilation). After main cables and rectifier plate inspection, engine taken on load. | 2024 | 2
| Blackout | 2024-02-03 | 13:15:00 | B | after annual maintenance of main gas meter, during changeover from KE to self generation; blackout occurred due to solar load shifted to self power and frequency down @ 48 Hz. | 2024 | 2
| Rental Eng. | 2024-02-02 | 14:30:00 | 48659 | Load Shed Activated during cabling disconnecting (Plant Lighting and Ventilatilation). | 2024 | 2
| G5 | 2024-01-30 | 18:15:00 | 89282 | Engine tripped on deviation low unit # 5.(Load Shed Activated(Plant Lighting and Ventilatilation). Just disconnected thermocouple and taken onload. | 2024 | 1
| G7 | 2024-01-26 | 09:20:00 | 77620 | Engine tripped on PO current diff.(Load Shed Activated(Plant Lighting and Ventilatilation) with FP6. Just reset engine and taken onload normally.customer complained gen set was trip with P.O Gen Diffrential current trip. Check diff current on terberg screen found L2 phase shows current diffrence 5 amperes while L1& L3 current diffrence zero ampere normal. Off load and stop gen set, checked gen set CT wiring and terminations found in alternator panel diffrential current CT terminals wire connectors rusted and lose connection. Properly cleand and installed back Diffrential CT wires. Gen set started and put on load up to 1000 Kw load and checked diff current found zero normal. Gen set put in normal plant operation, observed an houre found normal. | 2024 | 1
| G7 | 2024-01-24 | 14:40:00 | 77578 | Engine tripped on PO current diff.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine and taken onload normally. | 2024 | 1
| G2 | 2024-01-17 | 18:15:00 | 109830 | Engine tripped on Current high slow and fast.(Load Shed Activated(Plant Lighting and Ventilatilation). checked rectifier plate found one wire break so repaired and engine started/ taken onload @600kw but detonation appear on unit # 02; engine stopped and removed dynamo but detonation warning appear in unit # 01, 04, 16 and 20. next day Aesl team removed charging alternator pulley and drive from gen set and inspect found normal then installed back the drive and pulley. Check and Inspect the main alternator rectifier plate found normal. check the repaired wire found excitor rotor wire was last break from lugs then joint protect with heat shrink sleeves and installed back.Spark plugs of cylinder #1 & #2 replaced. Air filter elements cleaned and installed back. Gen set started and check at load up to 700 kw detonation warning comes then adjust the fuel parameter and increased load up to 1600 kw and observed found normal.again load decrease 400 kw and increase 1600 but no any detonation observed.genset running satisfactory condition.( fuel parameters as btu from 905 to 930 and correction factor from 95 to 97) | 2024 | 1
| Blackout | 2024-01-13 | 12:00:00 | B | gas engine # 01, 02, 04, 06 and 07 running onload 1300~1350 kw on 180 mbar gas pressure, so gas engine # 01 reduced load from 1350 to 300 due to gas pressure and load increased on other engines and blackout. | 2024 | 1
| G2 | 2024-01-12 | 20:20:00 | 109718 | Engine tripped on compressor bypass valve: abnormal update rate(1720-9) and throttle actuator invalid(1440-11), engine was on 1600+kw load.(Load Shed Activated(Plant Lighting and Ventilation). After reset engine and taken onload but engine again tripped on 500kw on compressor bypass valve: abnormal update rate(1720-9). checked and found one wire break near compressor bypass so after harness repairing engine started normally | 2024 | 1
| G6 | 2024-01-05 | 05:30:00 | 90169 | Engine tripped on shutoff valve failure .(Load Shed Activated(Plant Lighting and Ventilation). Due to cooling water header leaked on shutoff valve found malfuctioning, so replaced with new one. | 2024 | 1
| G4 | 2024-01-03 | 16:30:00 | 83113 | Followup from same date during alternator testing engine trippped on detonation @1700+kw, .(Load Shed Activated(Plant Lighting and Ventilation). | 2024 | 1
| G4 | 2024-01-02 | 16:30:00 | 82992 | Followup from same date during alternator testing engine trippped on CDVR, .(Load Shed Activated(Plant Lighting and Ventilation). After re-adjusted CDVR setting engine put onload normaly. | 2024 | 1
| Rental Eng. | 2023-12-29 | 15:20 | 48351 | Engine tripped on detonation unit # 04, .(Load Shed Activated(Plant Lighting and Ventilatilation). Air filter cleaned then started. | 2023 | 12
| Rental Eng. | 2023-12-29 | 17:55 | 48351 | Again Engine tripped after one hour on detonation .(Load Shed Activated(Plant Lighting and Ventilatilation). Reaplced detonation sensor unit 6/8 ad unit # 4 transformer. Then started | 2023 | 12
| G3 | 2023-12-26 | 21:30 | 101616 | Engine tripped on detonation unit # 05(voltage above normal, 1505-3), .(Load Shed Activated(Plant Lighting and Ventilatilation). Replaced respective sensor with new one then started engine. | 2023 | 12
| Rental Eng. | 2023-12-19 | 04:00 | 48088 | Engine tripped on detonation alarms, .(Load Shed Activated(Plant Lighting and Ventilatilation). After inspection, replaced detonation harness and exhaust bellows. | 2023 | 12
| Rental Eng. | 2023-12-18 | 19:30 | 48130 | Engine tripped on multiple alarms, .(Load Shed Activated(Plant Lighting and Ventilatilation). After changed BTU, started engine. | 2023 | 12
| Rental Eng. | 2023-12-15 | 04:00 | 48088 | Followup from dated 08.12.2023 tripping; Again Engine tripped, as per operator no any alarm.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset and started but again tripped. he rental service team Changed the detonation sensor of unit number 10 and 12 and then run the engine at 500 kW for 45 minutes. After 45 minutes the rental load has been increased and it has been taken to1000 kw, now engine behaviour found normal. | 2023 | 12
| Rental Eng. | 2023-12-08 | 05:02 | 47981 | Followup from dated 06.12.2023 tripping; Again Engine tripped on detonation unit # 09.(Load Shed Activated(Plant Lighting and Ventilatilation). PM carried outout by rental service then engine behaviour found normal. | 2023 | 12
| Rental Eng. | 2023-12-08 | 21:08 | 47981 | Followup from dated 06.12.2023 tripping; Again Engine tripped on detonation unit # 09.(Load Shed Activated(Plant Lighting and Ventilatilation). PM carried outout by rental service then engine behaviour found normal. | 2023 | 12
| G7 | 2023-12-08 | 23:08 | 76554 | Engine tripped on deviation unit # 09.(Load Shed Activated(Plant Lighting and Ventilatilation). Removed termocouple then engine behaviour found normal. | 2023 | 12
| Rental Eng. | 2023-12-06 | 18:27 | 47974 | Engine tripped on detonation unit # 09.(Load Shed Activated(Plant Lighting and Ventilatilation). 1. cleaned air filters 2. Adjusted BTUs 3. Adjusted tappets then engine behaviour found normal. | 2023 | 12
| G6 | 2023-11-29 | 19:30 | 89316 | Followup from dated PM; during load testing engine tripped on unit # 19 detonation alaram. (Load Shed Activated(Plant Lighting and Ventilatilation). after taken compression; unit # 19 compression found zero so, next day allied team will work on it. | 2023 | 11
| G7 | 2023-11-25 | 22:10 | 76282 | Gas Engine 7 tripped on multiple detonation alarm. (Load Shed Activated(Plant Lighting and Ventilatilation). After reset engine started but again engine Tripped on cylinder 20 deviation low .so disconnected thermocouple. engine started running on 600 kw under observation. engine tripped again at 600kw load. Load shade not operated. unit 1 detonation shutdown and unit # 18 and 20 deviation low. after cleaned unit # 18 and 20 spark plugs and reset engine then engine run on 1000kw. next day allied team will work on it.( after inspection on dated 26.11.2023 by allied engineering, unit # 18 and 20 compression found zero. | 2023 | 11
| Rental Eng. | 2023-11-20 | 19:30 | 47718 | Again Engine tripped on detonation unit # 05.(Load Shed Activated(Plant Lighting and Ventilatilation). 2nd time tripped on over speed and 3rd time tripped on detonation unit # 10, Adjusted fuel parameters then engine behaviour found normal. | 2023 | 11
| Rental Eng. | 2023-11-19 | 18:20 | 47700 | Engine tripped on shutoff valve.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine started normally. | 2023 | 11
| Rental Eng. | 2023-11-19 | 18:20 | 47700 | Again Engine tripped on shutoff valve.(Load Shed Activated(Plant Lighting and Ventilatilation). Adjusted fuel parameters then engine behaviour found normal. | 2023 | 11
| Rental Eng. | 2023-11-18 | 15:45 | 47672 | Engine tripped on shutoff valve.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine started normally. | 2023 | 11
| Rental Eng. | 2023-11-17 | 10:38 | 47668 | Engine tripped on detonation unit # 05.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine started normally. | 2023 | 11
| G2 | 2023-11-16 | 16:42 | 108364 | Engine tripped on Current high slow and fast.(Load Shed Activated(Plant Lighting and Ventilatilation). checked and found rectifier plate damage so replaced with new one engine started normally. | 2023 | 11
| Rental Eng. | 2023-11-16 | 18:10 | 47647 | Engine tripped on detonation unit # 05.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine started normally. | 2023 | 11
| G7 | 2023-11-12 | 23:52:00 | 75370 | Engine tripped on PO current diff.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine and taken onload normally. | 2023 | 11
| G2 | 2023-10-19 | 17:48:00 | 107714 | Engine tripped on Detonation unit # 13 and 15.(Load Shed Activated(Plant Lighting and Ventilatilation). On ET cylinder #13 detonation sensor: voltage below normal(1513-4), fuel shutoff valve: failure(17-12), throttle actuator invalid(1440-11), detonation unit #13(E413-1, E413-3),detonation unit #15(E415-1, E415-3). checked unit # 13, 15, 14 and 16 compression found okay so installed unit # 13/15 detonation sensor wire signal inside the ECM. after that engine started normally. | 2023 | 10
| G7 | 2023-10-11 | 19:55:00 | 75222 | Engine tripped on unit # 20 detonation shutdown. (Load Shed Activated(Plant Lighting and Ventilatilation). Preventively replaced transformer with old one then engine started and taklen onload normally. | 2023 | 10
| Rental Eng. | 2023-10-09 | 08:55:00 | 46952 | Engine tripped due to rental engine operator miscommunication.(Load Shed Activated(Plant Lighting and Ventilatilation) | 2023 | 10
| Rental Eng. | 2023-09-28 | 05:45:00 | 46746 | Engine tripped on inlet temperature.(Load Shed Activated(Plant Lighting and Ventilatilation), 2 time lighting load and 2 time with FP6. | 2023 | 9
| G3 | 2023-09-23 | 17:28:00 | 99386 | Followup from previous dated; Engine again tripped on same alarms as previous tripping, Engine Control Module: Abnormal Update rate(590-9) and Slave Electronic Module: Abnormal Update Rate(1636-9), Load Shed Activated(Plant Lighting and Ventilation Load) with FP6. all harness checked found ok so just engine reset then started engine normally | 2023 | 9
| G3 | 2023-09-22 | 17:15:00 | 99363 | Engine tripped on Engine Control Module: Abnormal Update rate(590-9) and Slave Engine #2 Electronic Module: Abnormal Update Rate(1636-9), Load Shed Activated(Plant Lighting and Ventilation Load) with FP6. all harness checked found ok so just engine reset then started engine normally. | 2023 | 9
| G2 | 2023-09-20 | 04:55:00 | 107024 | Followup from dated 16.09.2023; Engine again tripped on same fault: speed/ Timing sensor signal abnormal, Load Shed Activated(Plant Lighting and Ventilation Load) with FP6. as per allied staff, no any abnormality found maybe loose pin connection so renew respective sensor's all male female harnesss connection/ pins/ Master ECM/ slave ECM and signal after that engine then started engine normally.(during inspection, PM also done) | 2023 | 9
| G2 | 2023-09-16 | 11:55:00 | 106941 | Engine tripped on speed/ Timing sensor signal abnormal, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced respective sensor(p#5221642) but problem still. Allied team checked the speed timing sensor supply found 12v that is normal, checked the speed sensor/ timing sensor output to main ECM found normal while opened at sleeve ECM so laydown sensor output to slave ECM after that engine then started engine normally.(Note; as this scenario speed sensor found ok so respective sensor standby for next usage. | 2023 | 9
| G1 | 2023-09-07 | 09:15:00 | 119815 | Engine tripped during IPC replacement(due to wrong supply connection) .(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine then taken on normal load. | 2023 | 9
| G7 | 2023-09-06 | 04:15:00 | 74371 | Engine tripped due to diff. current alarm.(Load Shed Activated(Plant Lighting and Ventilatilation). Just reset engine then taken on normal load. | 2023 | 9
| Rental Eng. | 2023-08-28 | 10:35 | 46301 | Engine tripped on j/w temperature high, Load Shed Activated(Plant Lighting and Ventilation Load) with FP6. release air from system then started engine normally | 2023 | 8
| Rental Eng. | 2023-08-22 | 01:35 | 46264 | Engine tripped on detonation unit # 11, Load Shed Activated(Plant Lighting and Ventilation Load) with FP6. Replaced sensor then started engine normally | 2023 | 8
| Blackout | 2023-08-15 | 23:30 | B | Gas Engine # 01, 02, 03, 04, 05,06 and 07 with rental engine running onload @ 9.0 MW. sudden gas engine # 04 tripped with smell and some smook observed. alarms on Terberg as 1. PO Generator alarm 2. exitation disable by generator protection 3. PO generator voltage imbalance inverse trip 4. PO generator under frequency inverse trip, in same time blackout occured. after inspection, mechanically every thing is ok but main stator 2 coil found shortd so re-new both coils. | 2023 | 8
| G3 | 2023-08-04 | 1900 | 98222 | Engine tripped on Frequency low, Load Shed Activated(Plant Lighting and Ventilation Load). checked and found throttle connector loose so re-tighted and started engine normally. | 2023 | 8
| Rental Eng. | 2023-07-30 | 09:10 | 29303 | Engine tripped on detonation unit # 01, Load Shed Activated(Plant Lighting and Ventilation Load) with FP6. Replaced sensor then started engine normally | 2023 | 7
| G7 | 2023-07-22 | 02:00:00 | 75277 | Engine tripped on deviation low unit # 08, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced transformer(old one) then started engine normally | 2023 | 7
| Rental Eng. | 2023-07-17 | 16:00:00 | 29090 | FP3 and Niigata engine tripped during rental taken onload. Niigata Engine alarm Under voltage relay tripped, over current relay tripped. After inspection by rental service team, rectifier plate found damage so replaced (given by powerhouse inventory) and started engine normally. | 2023 | 7
| Rental Eng. | 2023-07-13 | 12:30 | 29005 | Engine tripped on detonation unit # 07, Load Shed Activated(Plant Lighting and Ventilation Load). Just interchanged sensor then started engine normally | 2023 | 7
| G5 | 2023-07-03 | 22:00 | 84866 | Engine tripped on deviation low unit # 20, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced transformer(old one)/ spark plug(new) and disconnected thermocouple preventively then started engine normally | 2023 | 7
| G6 | 2023-06-26 | 00:50 | 85657 | Engine tripped on detonation unit # 10, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced transformer with old one preventively then started engine normally | 2023 | 6
| Rental Eng. | 2023-06-18 | 08:50 | 28681 | Engine tripped on detonation unit # 10, Load Shed Activated(Plant Lighting and Ventilation Load). Disconnected respective sensor then started engine normally | 2023 | 6
| G7 | 2023-06-14 | 12:30:00 | 72446 | Engine tripped during load test after preventive maintenance ( tripped on PO alarms), Load Shed Activated(Plant Lighting and Ventilation Load). Reset and started engine normally | 2023 | 6
| Rental Eng. | 2023-05-30 | 07:10 | 28440 | Engine tripped on oil diff. pressure high, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced oil filters then started engine normally | 2023 | 5
| Rental Eng. | 2023-05-30 | 15:45 | 28448 | Engine tripped on no any alarm, Load Shed Activated(Plant Lighting and Ventilation Load). Just reset engine then started engine normally | 2023 | 5
| G4 | 2023-05-20 | 14:30 | 81086 | Engine tripped on DE bearing temprature sudden high from normal to 173.5, Load Shed Activated(Plant Lighting and Ventilation Load). After inspected respective wire found damage so de-active alarm from Terberg then started engine normally | 2023 | 5
| Rental Eng. | 2023-05-11 | 17:10:00 | 27361 | Engine tripped on detonation unit # 09, Load Shed Activated(Plant Lighting and Ventilation Load). Disconnected respective sensor then started engine normally | 2023 | 5
| Blackout | 2023-04-02 | 13:30 | B | during load shifting from KE to self power , gas engine # 01, 04, 06 and 07 was running. | 2023 | 4
| Rental Eng. | 2023-03-24 | 04:10:00 | 27361 | Engine tripped on detonation unit # 11, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced respective sensor then started engine normally | 2023 | 3
| Rental Eng. | 2023-03-24 | 11:00:00 |  | Engine again tripped on over speed shutdown, Due to Low Load, Load Shed Not Activated(Plant Lighting and Ventilation Load). Throttle found on 100% so reset then started engine normally | 2023 | 3
| Rental Eng. | 2023-03-12 | 05:05:00 | 104713 | Engine tripped on deviation low unit # 01, Load Shed Activated(Plant Lighting and Ventilation Load). Disconnected thermocouple then started engine normally | 2023 | 3
| Rental Eng. | 2023-03-06 | 23:30:00 | 26927 | Engine tripped, Load Shed Activated(Plant Lighting and Ventilation Load). No any alaram appear so Reset and started engine normally | 2023 | 3
| Rental Eng. | 2023-03-06 | 12:15:00 | 26927 | Engine tripped on deviation low unit # 09, Load Shed Activated(Plant Lighting and Ventilation Load). Replaced air filters then started engine normally | 2023 | 3
| G7 | 2023-02-19 | 03:55 | 70069 | Engine tripped on 600-PO generator alarm/ 0643-PO generator differential current trip/ 085- excitation is disable by generator protection, Load Shed Activated(Plant Lighting and Ventilation Load). Reset and started engine normally | 2023 | 2
| G7 | 2023-02-19 | 23:20 | 70077 | Engine tripped on 600-PO generator alarm/ 0643-PO generator differential current trip/ 085- excitation is disable by generator protection, Load Shed Activated(Plant Lighting and Ventilation Load). As per instruction of laung sb, tomorrow morning allied will check. | 2023 | 2
| Rental Eng. | 2023-01-17 | 07:00:00 | 26216 | Engine tripped on detonation unit # 11, Load Shed Activated(Plant Lighting and Ventilation Load). Reset and started engine normally | 2023 | 1
| Rental Eng. | 2023-01-15 | 21:55:00 | 26183 | Engine tripped on detonation unit # 01, Load Shed Activated(Plant Lighting and Ventilation Load). Reset and started engine normally | 2023 | 1
| Rental Eng. | 2023-01-12 | 23:45:00 | 26153 | Engine tripped on detonation unit # 11, Load Shed Activated(Plant Lighting and Ventilation Load). Reset and started engine normally | 2023 | 1
| G7 | 2023-01-11 | 07:45:00 | 69240 | Engine tripped on GECM 289, throttle actuator abnormal update rate(1440-9), Load Shed Activated(Plant Lighting and Ventilation Load). Throttle connector found loose. Replaced throttle with repaired one then taken onload normally. | 2023 | 1
| G3 | 2023-01-08 | 16:25 | 94373 | Engine tripped on GECM 289, no any alarm on ET, Load Shed Activated(Plant Lighting and Ventilation Load). After physically inspection/ re-set engine then taken onload normally. | 2023 | 1
| G7 | 2023-01-04 | 22:45 | 69087 | Engine tripped on GECM 289, throttle actuator abnormal update rate(1440-9), Load Shed Activated(Plant Lighting and Ventilation Load). Throttle connector found loose so re-tigght/ re-set engine then taken onload normally. | 2023 | 1
| G5 | 2025-02-01 | 17:15:00 | 96984 | Engine tripped on GECM alarm. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. No alarm on ET and Terberg, Reset engine taken onload normally | 2025 | 2
| G2 | 2025-05-01 | 16:35:00 | 114336 | Engine tripped on GECM shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. On ET detonation Derate requested (E253-2) and detonation appear on unit # 11, 07, 17, 09, 05, 10 and 18. engine tripped on unit # 11 but secondry voltage was down in unit # 05( from 25 to 19.7)/ Check alarm history, detonation alarm found in several cylinders and and genset tripped on cylinder no. 11 detonation shutdown.Remove all cylinders ignition transformers, spark plugs.Inspect the cylinders no. 05 & 07 with bore scope found satisfactory.Measure the all cylinders compression pressure found between 240psi to 260psi. Check and adjust the valves clearance of cylinder no. 05 & 07. Swap the cylinder no. 05/07 detonation sensor with cylinder no. 02/04. Swap the ignition transformers of cylinder no. 05/07 with 08/14. Swap the spark plugs if cylinder no. 05/07 with 18/10. Start the genset and put on load upto 1300kw, maximum providing load by customer due to unavailability of load shed. check all running parameters found satisfactory. (43 times detonation alarm appears at cylinder no. 05 between 111268 to 114340 hours) | 2025 | 5
| Rental Eng. | 2025-01-15 | 17:10:00 | 52553 | Engine tripped on detonation unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced sensor with new one and taken onload. | 2025 | 1
| N1 | 2025-01-26 | 15:40:00 | 42931 | Engine tripped on load veriation 200 to 900kw. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked fuel pressure, temperature found ok. Cleaned indication filter, flow meter filter and main filters but problem as it is. | 2025 | 1
| N1 | 2025-01-27 | 15:40:00 | 42931 | Follow from 26.01.2025 Niigata 1 Tripping; GaddiBaan satff replaced Governor but same load veriation as per previous and Engine tripped on load veriation 200 to 900kw. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked fuel pressure, temperature found ok. Cleaned indication filter, flow meter filter and main filters but problem as it is. | 2025 | 1
| G4 | 2025-01-28 | 15:15:00 | 35599 | Engine tripped on detonation unit # 12 and 9 hours ago Transformer primary 8 Current above normal apprear. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced unit # 8 transformer with old one and unit # 12 spark plug cleaned then engine started normally | 2025 | 1
| G2 | 2025-07-02 | 00:20:00 | 115083 | Sunden load veriation observed from 1100 to 100kw. After inspection unit # 01, 02, 05, 07, 09, 11, 15, 17, 18 compression found zero. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. | 2025 | 7
| G4 | 2025-07-02 | 21:30:00 | 92384 | Engine tripped on deviation low unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. Just cleaned spark plug and check transformer resisitance, found ok. Preventively disconnected respective thermocouple engine taken onload. | 2025 | 7
| G3 | 2025-02-15 | 02:05:00 | 111200 | Engine tripped on fuel metering module failure. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode. Replaced fuel valve with repaired one (Repaired from Munfrid Engineering). after work engine started and taken onload under observation on 600kw after satisfactory operation engine kept as parallel to other engines. | 2025 | 2
| G3 | 2025-02-16 | 03:10:00 | 111214 | Engine again tripped on fuel metering module failure. Load Shed Activated.(Plant Lighting and Ventilatilation) and CPP Thread Mode with FP6. Just reset engine and taken onload under observation on 600kw after satisfactory operation engine kept as parallel to other engines. | 2025 | 2
| G3 | 2025-02-16 | 16:10:00 | 111222 | Engine 3rd time again tripped on fuel metering module failure. Load Shed Activated.(Plant Lighting and Ventilatilation) and CPP Thread Mode with FP6. Replaced fuel valve with an other repaired one (Repaired from Munfrid Engineering). after work engine started and taken onload under observation on 600kw after satisfactory operation engine kept as parallel to other engines. Preventively Throttle Harness (p# 305-0580) replaced with new one due to threads damage. | 2025 | 2
| G8 | 2025-02-23 | 00:45:00 | 36596 | Engine tripped on over speed. Load Shed Activated.(Plant Lighting and Ventilatilation), FP6 with CPP. No any abnormality found so just re-set engine then taken onload. | 2025 | 2
| G2 | 2025-02-23 | 05:10:00 | 115093 | Sunden load veriation observed from 1300 to 400kw. Load Shed Activated.(Plant Lighting and Ventilatilation) FP6 with CPP Thread Mode. Customer complained about load variation problem. Check the historical alarms and graphs. For testing Interchange throttle actuator and fuel valve from other Genset. Also install new compressor bypass actuator motor and couple the old shaft. Remove tappet covers ignition transformers and spark plugs. Install new spark plugs (P/No. 602-7619, Qty = 20) in all cylinders. After doing so install back all ignition transformers and tappet covers. Lay down new wires for voltage and speed control. Also ENERCON engineer visit the site and interchange DEIF Generator controller from other Genset panel. After that start the Genset found started normally check all parameters found normal then Genset put on load up to 800kW found after some time Terberg engine parameters disappeared as well as the data of EMCP II+ disappeared. Offload stopped the Genset. Change datalink wire but no data appeared. Change CCM (new) and EMCP from other Genset but problem remain same. However when Terberg data link removed EMCP parameters appeared. Start the Genset and put on load up to 1000kW found running normally. EMCP to Terberg communication problem need to be addressed | 2025 | 2
| G6 | 2025-03-03 | 07:30:00 | 97255 | Engine tripped on detonation unit # 15. Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with CPP Thread Mode. Replaced respective detonation sensor due to wire damage and engine taken onload. | 2025 | 3
| Blackout | 2025-04-03 | 08:15:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 6,7, 8 and 09) running on normal load, Black shutdown due to gas engine 5 blue HT wire break. | 2025 | 4
| Rental Eng. | 2025-04-03 | 16:15:00 | 52951 | Engine tripped on over speed. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. One CT found damage so replaced with new one and taken onload. | 2025 | 4
| G1 | 2025-07-03 | 16:16:00 | 131101 | Engine tripped on detonation unit # 05 voltage above normal. Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with CPP Thread Mode. Replaced respective detonation sensor with new one and engine taken onload. | 2025 | 7
| Blackout | 2025-11-03 | 23:20:00 | B | all gas engines ( GE1, 2, 3, 4, 6,7, 8, 9 and rental engine) running on normal load, Black shutdown due to gas engine 7 red HT wire break. | 2025 | 11
| Blackout | 2025-03-14 | 02:36:00 | B | all gas engines ( GE1, 2, 3, 4, 6,7, 8, 9 and rental engine) running on normal load, Black shutdown due to gas engine 7 yellow HT wire break and main coupling damage. | 2025 | 3
| G9 | 2025-03-16 | 16:16:00 | 131101 | Engine tripped on Earth Fault Trip Signal from Terberg 7. Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with CPP Thread Mode. Just Re-set engine then taken onload. | 2025 | 3
| G2 | 2025-03-17 | 09:25:00 | 115554 | Engine tripped on CDVR shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Checked alternator main cables, CTs wires, any loosness; no any abnormality found. Check Exciter, PMG, Rectifier and sensing wires found normal./ At the time of visit on site gen set was in stop condition, customer complained that Genset was trip with Terberg panel alarm of Cdvr shutdown and Cdvr red LED was found blinking. Customer physical checked power cables terminals and rectifier plate found normal. Customer reset the Genset started and checked on load up to 500 kw found normal then off load and stop. AESL team check logged alarms in ET, no any recently shutdown was found in ET. Remove alternator cover and checked rectifier plate diodes and veristar found normal. Check and clean PMG and exciter wiring and installed back. Check PMG and exciter wiring in between wall mounted EMCP2 panel and alternator panel found a wire abrasion and Short to body ground marks the properly insulated the wire. Check and clean CDVR connectors and installed back. Installed back alternator cover and gen set started and check off load parameters found normal, genset put on load 500 kw and observed found normal, genset load increased Upto 850 kw found normal. | 2025 | 3
| G2 | 2025-03-24 | 17:45:00 | 115723 | Engine again tripped on CDVR shutdown. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. | 2025 | 3
| Rental Eng. | 2025-04-17 | 10:35:00 | 53318 | Engine tripped on Detonation unit # 04. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. adjusted BTU and correcting factor taken onload. | 2025 | 4
| G9 | 2025-04-20 | 00:00:00 | 6481 | Engine tripped during gas engine # 07 junction box 25A breaker ON. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. just reset engine and engine 7 side 35A bearker off then engine 9 taken onload normally. | 2025 | 4
| G2 | 2025-04-21 | 11:40:00 | 116117 | Engine again tripped on CDVR shutdown( loss of excitation, reverse VAR). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Interchanged CDVR with gas engine # 07 for testing/ observation purpose (CDVR power supply interchanged from Terberg to Engine side) | 2025 | 4
| Rental Eng. | 2025-04-22 | 11:55:00 | 53438 | Engine tripped on Deviation high unit # 08 and 10. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. adjusted BTU and correcting factor taken onload. | 2025 | 4
| G3 | 2025-11-05 | 22:20:00 | 113079 | Engine tripped on Engine oil diff. pressure low (E128-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. replaced oil assembly with engine # 07 (gas engine # 07 already on TE) then taken onload. | 2025 | 11
| G1 | 2025-05-14 | 17:22:00 | 132572 | Engine tripped on Throttle abnormal update rate. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced preventively throttle harness with new one/ main harnesss slightly short near fuel valve connector so properly tapped then Engine started/ kept as parallel to other engines. | 2025 | 5
| G9 | 2025-05-23 | 14:05:00 | 7268 | Engine tripped on turbo1 temperature high (681 temperature), there was an 850 kW load on Gas Engine9. Load Shed Activated.(Plant Lighting and Ventilatilation) with Ereema4. Reset then Engine started/ kept as parallel to other engines. | 2025 | 5
| G1 | 2025-05-25 | 11:20:00 | 132828 | Engine tripped on turbo charger bypass valve actuator abnormal update rate. Load Shed Activated.(Plant Lighting and Ventilatilation) with Ereema4. Replaced Bypass actuator valve replace with G7 (G7 already on TE),reset the engine and back onload normal. | 2025 | 5
| G1 | 2025-05-26 | 03:10:00 | 132841 | Engine 1 tripped on multiple cylinders low /high deviation and back fired ,there was 2500kw load jerkobserved from plant side (Line 5 emergency stopped) at that moment G1 tripped. Load Shed Activated.(Plant Lighting and Ventilatilation) with Ereema4. After that when they start the Genset deviating low alarms appeared in different cylinders.Check the engine parameters and sensors, after wiggle test found manifold pressure values changes. | 2025 | 5
| G2 | 2025-05-30 | 09:10:00 | 117018 | Gas engine # 01 Tripped on Protection Relay(L1, Red). Load Shed Activated(Plant Lighting and Ventilation Load) with Ereema4. replaced with New protection relay with new brand(DEIF, S/N 2137441.0001/ Type: RMC-131D/ Order# 921005295.30/ Item 2913160660.01) provided by Enercon and installed by Mr. Rizwan (Enercon staff). new relay connections diagram attached in Terberg drawing. | 2025 | 5
| G9 | 2025-05-31 | 10:45:00 | 7457 | Engine tripped during line5 sudden complete off (@ 5000Kw load reduced). Load Shed Activated(Plant Lighting and Ventilation Load) with Ereema4. | 2025 | 5
| G4 | 2025-10-06 | 03:00:00 | 94855 | Engine tripped on CDVR shutdown. Load Shed Activated(Plant Lighting and Ventilation Load) with Ereema4 and complete CPP feeder. Total load cut @ 800kw due to only line 4 was running during eid holidays. Checked main alternator wires/ CTs controlling and rectifier plate. rectifier plate's one wire found broken so fixed then started and taken onload. | 2025 | 10
| G6 | 2025-06-14 | 23:30:00 | 99698 | Engine tripped on engine oil temprature high to coolant differance. Load Shed Activated(Plant Lighting and Ventilation Load) with FP6 and CPP feeder. Checked and found jacket water temprature sensor rusty so replaced with old one then started and taken onload. | 2025 | 6
| G3 | 2025-06-15 | 22:15:00 | 113684 | Engine tripped on throttle actuator failure. Load Shed Activated(Plant Lighting and Ventilation Load) with FP6 and CPP feeder. throttle found jamed so Replaced throttle with repaired one( repaired by munfrid engineering) then started and taken onload. | 2025 | 6
| G9 | 2025-06-16 | 13:00:00 | 7838 | Engine tripped on Jw inlet temprature high (during project team work). Load Shed Activated(Plant Lighting and Ventilation Load) with FP6 and CPP feeder. Just reset and taken onload. | 2025 | 6
| Rental Eng. | 2025-06-21 | 03:28:00 | 53662 | Engine tripped on exhaust temprature high unit # 01. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. just disconnected thermocouple and taken onload. | 2025 | 6
| Blackout | 2025-06-21 | 20:48:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 6, 8, 9 and rental engine) running on normal load, Black shutdown occurred. No any reason found. | 2025 | 6
| G1 | 2025-01-07 | 22:20:00 | 133635 | Engine tripped on unit # 06 detonation sensor failure. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced sensor with new one and back onload normal. | 2025 | 1
| G1 | 2025-02-07 | 10:30:00 | 133647 | Engine tripped on throttle and acutator bypass abnormal update rate. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced throttle with repaired one and back onload normal. | 2025 | 2
| G3 | 2025-05-07 | 08:54:00 | 114161 | Engine tripped on lube oil diff. pressure low. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced both side sensors with ones and back onload normal. | 2025 | 5
| Blackout | 2025-07-07 | 14:48:00 | B | all gas engines ( GE1, 2, 3, 4, 5, 6, 7, 8, 9) running on normal load, Black shutdown occurred. Gas engine # 05' Red and neutral wire found broken, NDE side bearing bkoken and DE side bearing slipped. | 2025 | 7
| G1 | 2025-09-07 | 20:30:00 | 133820 | Engine tripped on unit # 18/20 detonation sensor failure. Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced sensor with new one and back onload normal. | 2025 | 9
| G5 | 2025-07-15 | 08:25:00 | 99273 | Engine tripped on compressor bypass valve actuator: abnormal update rate(1720-9), fuel metering module failure(1446-12), throttle actuator: abnormal update rate(1440-9). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced overhauled fuel valve (from munfrid engineering) and replaced throttle harness with new one preventively. | 2025 | 7
| G5 | 2025-07-28 | 08:15:00 | 99482 | Engine tripped on fuel metering module failure(1446-12), fuel metering module: current below normal(1446-5). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Thottle connector found loose so retighted and Reset engine then taken onload. | 2025 | 7
| G5 | 2025-07-30 | 12:35:00 | 99501 | 3rd time Engine tripped on fuel metering module failure(1446-12), fuel metering module: current below normal(1446-5). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced main harness with new one due to suspected. | 2025 | 7
| G8 | 2025-01-08 | 19:10:00 | 39336 | Engine tripped on detonation shutdown on unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced detonation sensor with used one preventively and replaced spark plug with new. | 2025 | 1
| G5 | 2025-08-08 | 05:10:00 | 99680 | Engine tripped on Emergency stop activated (E 264-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Reset engine and taken on load. | 2025 | 8
| G5 | 2025-08-08 | 09:28:00 | 99685 | 2nd time again Engine tripped on Emergency stop activated (E 264-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Laydown new emergency stop wire from connector to ECM and taken on load. | 2025 | 8
| G8 | 2025-10-08 | 21:52:00 | 39553 | Engine tripped on detonation shutdown unit # 12 (E432-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced unit # 12 spark plug with new and taken onload. | 2025 | 10
| G8 | 2025-08-17 | 20:00:00 | 39716 | Engine tripped on detonation shutdown unit # 01. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. interchanged spark plug with unit # 04 and taken onload. After 01 hr detonation appear on unit # 04 so replaced spark plug with new one in respective unit and taken onload. | 2025 | 8
| Blackout | 2025-08-22 | 11:20:00 | B | Blackout due to Enercon Master Panel and gas engine control panel 02's Battery charger failure.( enercon system complete down). | 2025 | 8
| G3 | 2025-08-22 | 16:30:00 | 115248 | after balckout engine started and taken on load but load variation observed from 300 to 900Kw so stoped the engine and replaced manifold inlet pressure sensor and its harness with new one but problem still. as per allied replaced fuel valve with repaired one by Munfrid engineering, after half an hour engine tripped on fuel mertering module: current below normal (1446-5) and fuel mertering module: failure (1446-12). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. so again fuel valve replaced with repaired one by Munfrid enginnering, after that engine behaviour found normal. | 2025 | 8
| Blackout | 2025-08-23 | 00:40:00 | B | Blackout due to short circuit in KE utility 1(Q2). as per Enercon report; G9 tripped on over current 1st then other engines tripped by Terberg on phase protections. | 2025 | 8
| G3 | 2025-05-09 | 18:30:00 | 115571 | Followup from dated 22.08.2025 tripping; Engine again tripped on fuel mertering module: current below normal (1446-5) and fuel mertering module: failure (1446-12). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. so again fuel valve replaced on dated 08.09.2025 with repaired one by Munfrid enginnering, after that engine behaviour found normal. | 2025 | 5
| G5 | 2025-12-09 | 06:45:00 | 100261 | Engine again tripped on High Left Terbocharger Turbine Outlet Temprature ( E243-3), High Left Terbocharger Turbine Outlet Temprature: Voltage Below Normal ( 1489-4), High Left Terbocharger Turbine Outlet Temprature: Current Below Normal ( 1489-5). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Terbocharger Turbine Outlet Temprature sensor harness found short so fixed with PVC tape and engine started and taken onload. | 2025 | 12
| G9 | 2025-09-13 | 07:40:00 | 9944 | Engine tripped Engine fuel differential pressure: Low: most serve (3) 1391-1/ Engine fuel differential pressure: Low: moderate severity (1) 1391-18. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. (removed gas regulation diaphram impact found normal. engine try to start but found gas street soliod only one valve operate. removed and checked solinoid connection and inspect harness found normal. cleaned ECM box's mounted harness connnection after that both solinoid valves operate normal. engine tested on 1650kw found all parameters with in range. | 2025 | 9
| G4 | 2025-09-15 | 11:20:00 | 96951 | Engine on Rear bearing temperature high. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Juction box connections found malfuctioning so re-tighted all connections then taken onload. | 2025 | 9
| G4 | 2025-09-15 | 18:00:00 | 96952 | Engine again tripped on same fault; Rear bearing temperature high. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Just bypass both side bearing temperature sensor then taken onload. | 2025 | 9
| G8 | 2025-09-19 | 18:42:00 | 40454 | Engine tripped on detonation unit # 05. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced drtonation sensor with new one/ spark plug replaced with old one then taken onload. | 2025 | 9
| G8 | 2025-01-10 | 19:12:00 | 40744 | Engine tripped on detonation shutdown unit # 12 (E432-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced unit # 12 spark plug with new and taken onload. | 2025 | 1
| G3 | 2025-08-10 | 12:00:00 | 116073 | Engine tripped on throttle acutator abnormal update rate (1440-9). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6. Replaced throttle with repaired one and replaced its Harness with new one and back onload normal. | 2025 | 8
| G9 | 2025-12-10 | 16:40:00 | 10641 | Engine tripped during gas engine 8 loading process( UVT malfunctioning). Load Shed Activated.(Plant Lighting and Ventilatilation) with CPP Thread Mode and FP6 with LG Chiller. Replaced uvt. | 2025 | 12
| Blackout | 2025-10-18 | 22:10:00 | B | Gas Generator Control Panel 2: due to malfuctioning of Voltage Level Relay(DC-27), master panel power supply OFF so replaced with new one. After that system behaviour is normal. | 2025 | 10
| G2 | 2025-05-11 | 04:27:00 | 120545 | Sudden engine reverse power and tripped ( Load Shed Activated.(Plant Lighting and Ventilatilation) and FP6 with LG Chiller.) and save blackout with manually operate loadshed for CPP thread mode. After inspection found that shutoff valve malfuctioning/ not working properly so replaced with repaired (repaired by munfrid engineering) one/customer complained about generator Reverse power last night. Check the historical alarms and ET codes found low fuel pressure and low gas fuel differential pressure. Manually check the gas solenoid found not working. | 2025 | 5
| G8 | 2025-11-21 | 20:50:00 | 41714 | Engine tripped on deviation low unit # 12 (E852-3). Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced unit # 12 spark plug with new and taken onload. | 2025 | 11
| G7 | 2025-12-12 | 02:42:00 | 90140 | Engine tripped on deviation unit # 15. Load Shed Activated.(Plant Lighting and Ventilatilation) with FP6. Replaced spark plug with new one/ checked ignition transformer found ok then taken onload. | 2025 | 12
| G2 | 2025-12-17 | 02:50:00 | 121491 | suddenly dropped from 1100 kw to 200 kw and Engine tripped on fuel valve malfuctioning and detonation alarm appear in unit # 3,17, 2,4, 12, 18 6, 14. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. After inpection fuel valve connector found loose so retighted with wire and taken onload. | 2025 | 12
| G3 | 2025-12-25 | 22:00:00 | 117227 | Engine Tripped on protection relay. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. Replaced protection relay with new one. | 2025 | 12
| G1 | 2025-12-28 | 17:40:00 | 137077 | Engine Tripped on deviation high unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. After checked spark plug and transformer and removed thermocouple; engine taken on load normally | 2025 | 12
| Blackout | 2026-11-01 | 08:10:00 | B | Blackout due to gas pressure zero. | 2026 | 11
| G2 | 2026-01-17 | 12:00:00 | 122124 | Engine Tripped on deviation high unit # 12. Load Shed Activated.(Plant Lighting and Ventilatilation) with LG Chiller Mode and FP6. during inspection one wire found short in generator control cable juction box; after proper tapping engine taken on load normally | 2026 | 1